INTRINSIC SAFETY (IS) INFORMATION

Intrinsic safety is a requirement that may be applicable to devices that are being operated in areas with flammable gases or fuels. It means the device is incapable of igniting those gases.

Intrinsically safe equipment must carry a label, which specifies the exact I-Safe rating for the equipment and the name of the NRTL (Nationally Recognized Testing Laboratory) who tested it. Testing laboratories have very stringent certification requirements that vary according to the level of I-Safe approval desired. Therefore, each intrinsically safe device is certified for different levels of I-Safe approval, and can only be used in specific hazardous environments

Intrinsically Safe approval certifications are made up of multiple classes, groups and divisions that correspond to the specific hazardous environment a device is approved to operate in. Each class consists of two divisions and certain classes have multiple groups.

| Classes |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Class I |  | Flammable gases or vapors are present in the air in quantities sufficient to produce explosive or ignitable mixtures. |  |  |  |
| Class II |  | Combustible or conductive dusts are present. |  |  |  |
| Class III |  | Ignitable fibers or flyings are present, but not likely to be in suspension in sufficient quantities to produce ignitable mixtures. (Group classifications are not applied to this class.) |  |  |  |
| Divisions |  |  |  |  |  |
| Division 1 | The substance referred to by class is present during normal conditions. |  |  |  |  |
| Division 2 | The substance referred to by class is present only in abnormal conditions, such as a container failure or system breakdown. |  |  |  |  |
| Groups |  |  |  |  |  |
| Group A |  |  | Acetylene |  |  |
| Group B |  |  | Hydrogen (or gases of equivalent hazard) |  |  |
| Group C |  |  | Ethylene (or gases of equivalent hazard) |  |  |
| Group D |  |  | Gasoline (or gases of equivalent hazard) |  |  |
| Group E |  |  | Metal Dust |  |  |
| Group F |  |  | Coal Dust |  |  |
| Group G |  |  | Grain Dust |  |  |
| Temperature Codes |  |  |  |  |  |
|  |  |  |  | ° F | ° C |
| T1 |  |  |  | 842 | 450 |
| T2 |  |  |  | 572 | 300 |
| T3 |  |  |  | 392 | 200 |
| T4 |  |  |  | 275 | 135 |
| T5 |  |  |  | 212 | 100 |
| T6 |  |  |  | 185 | 85 |